## LH-1
Cooling Load Calculation:-
Design Conditions:- |  |  | Given Data:-
Location | Guwahati |  | Room Entering air Temp.
Outdoor DBT | 35°C |  | Coil Temp. | 7°C
Outdoor RH | 80% |  | Recirculation | 70%
Indoor DBT | 25°C |  | Max/Min temperature | 37°C/27°C
Indoor RH | 55% |  | Range | 10°C
Wind Velocity | 3.1 Kmph |  | Maximum outdoor | 37°C
Month under consideration | July |  | Mean outdoor temperature | 32°C
Calculation for Lecture hall 1:-
Specifications(In SI Units):- |  |  | Quantity |  | Total Rated Power(W)
Lights |  |  | 50(each 100W)
Speakers |  |  | 10(Each 150W) | 13 inch | 1500
PC |  |  | 1(90W) | 15 inch TFT display | 90
Projector and UPS |  |  | 500W | (3000-4000 lumen) | 500
No of Persons |  |  | 250 | 17-40 years age group
Calculations for Structures:-
WALLS
Type | Length (ft) | Height (ft) | Area (ft^2) | Door/Window | Remaining area | CLTD/TD | Inside design Temp (TR) | Mean outdoor Temp (TM) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
NORTH | 25 | 30 | 750 | 0 | 750 | 18 | 77 | 89.6 | 18 | 0.156 | 2106
NORTH WEST | 25 | 30 | 750 | 1 Door | 675 | 18 | 77 | 89.6 | 18 | 0.156 | 1895.4
WEST | 25 | 30 | 750 | 0 | 750 | 18 | 77 | 89.6 | 18 | 0.156 | 2106
SOUTH WEST | 25 | 30 | 750 | 1 Door | 675 | 33 | 77 | 89.6 | 38.6 | 0.156 | 4064.58 | FACING SUN
SOUTH | 25 | 30 | 750 | 0 | 750 | 33 | 77 | 89.6 | 38.6 | 0.156 | 4516.2
SOUTH EAST | 25 | 30 | 750 | 1 Door | 675 | 18 | 77 | 89.6 | 23.6 | 0.156 | 2485.08
EAST | 25 | 30 | 750 | 0 | 750 | 18 | 77 | 89.6 | 18 | 0.156 | 2106
NORTH EAST | 25 | 30 | 750 | 1 Door | 675 | 18 | 77 | 89.6 | 18 | 0.156 | 1895.4
[10 empty] | Total | 21174.66
ROOFS
Type | Length (ft) | Area (ft^2) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
Concrete roof on which clay tiles are placed with false ceiling and sound absorbing material | 25 | 3018 | 33 | 0.14 | 13943.16
FLOOR
Type | Length (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load
Concrete flooring with tiles | 25 | 3018 | 9 | 0.345 | 9370.89
DOORS
Type | Length (ft) | Width (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load | 4 Doors
Aluminium Door | 8 | 4 | 32 | 18 | 2.51 | 1445.76 | 5783.04
Calculations for People:-
Type | Persons | SHG/LHG | CLF | Cooling load
Sensible | 250 | 210 | 0.3 | 15750
Latent | 250 | 140 | 1 | 35000
Calculations for Lights:-
Type | Conversion factor | Rated Power | CLF | Ballast Factor | Number of lights | Cooling load
100 W LED bulbs | 3.4 | 100 | 1 | 1.3 | 50 | 22100
Calculations for Appliances:-
Sensible
Type | Conversion factor | Rated Power | CLF | Usage factor | Radiation factor | Quantity | Cooling load
Speakers | 3.4 | 150 | 1 | 1 | 0.15 | 10 | 765
PC | 3.4 | 240 | 0.4 | 0.3 | 0.15 | 1 | 14.688
Projector and UPS | 3.4 | 500 | 0.4 | 0.3 | 0.2 | 1 | 40.8
[6 empty] | Total | 820.488
Calculations for Ventilation:-
Type | Constant | CFM | TD( To-Tc) | Number of persons | Cooling load
Sensible | 1.08 | 5 | 34.2 | 250 | 46170
Type | Constant | CFM | HD( Wo-Wc) | Number of persons | Cooling load
Latent | 4840 | 5 | 0.0185 | 250 | 111925
Calculations for Infiltration:-
Type | Constant | CFM | TD( To-Tc) | Number of persons | Cooling load
Sensible | 1.08 | 5 | 18 | 250 | 24300
Type | Constant | CFM | HD( Wo-Wi) | Number of persons | Cooling load
Latent | 4840 | 5 | 0.0177 | 250 | 107085
Summary
Cooling Load Components | Sensible load | Latent load | TOTAL LOAD IN Btu/hr
WALLS | 21174.66 | 0 | 21174.66
ROOFS | 13943.16 | 0 | 13943.16
FLOOR | 9370.89 | 0 | 9370.89
DOORS | 5783.04 | 0 | 5783.04
LIGHTS | 22100 | 0 | 22100
PEOPLE | 15750 | 35000 | 50750
APPLIANCES | 820.488 | 0 | 820.488
INFILTRATION | 24300 | 107085 | 131385
VENTILATION | 46170 | 111925 | 158095
Total | 159412.238 | 254010 | 413422.238 | TONNES OF REFERIGERATION
Room Total sensible Load | 88942.238 |  |  | 34.4519
Room Total latent Load |  | 35000
Total room load |  |  | 123942.238
Sensible heat factor | 0.71761

## LH-2
Cooling Load Calculation:-
Design Conditions:- |  |  | Given Data:-
Location | Guwahati |  | Room Entering air Temp.
Outdoor DBT | 35°C |  | Coil Temp. | 7°C
Outdoor RH | 80% |  | Recirculation | 70%
Indoor DBT | 25°C |  | Max/Min temperature | 37°C/27°C
Indoor RH | 55% |  | Range | 10°C
Wind Velocity | 3.1 Kmph |  | Maximum outdoor | 37°C
Month under consideration | July |  | Mean outdoor temperature | 32°C
Calculation for Lecture hall 1:-
Specifications(In SI Units):- |  |  | Quantity |  | Total Rated Power(W)
Lights |  |  | 50(each 100W)
Speakers |  |  | 10(Each 150W) | 13 inch | 1500
PC |  |  | 1(90W) | 15 inch TFT display | 90
Projector and UPS |  |  | 500W | (3000-4000 lumen) | 500
No of Persons |  |  | 250 | 17-40 years age group
Calculations for Structures:-
WALLS
Type | Length (ft) | Height (ft) | Area (ft^2) | Door/Window | Remaining area | CLTD/TD | Inside design Temp (TR) | Mean outdoor Temp (TM) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
NORTH | 25 | 30 | 750 | 0 | 750 | 18 | 77 | 89.6 | 18 | 0.156 | 2106
NORTH WEST | 25 | 30 | 750 | 1 Door | 675 | 18 | 77 | 89.6 | 18 | 0.156 | 1895.4 | FACING SUN
WEST | 25 | 30 | 750 | 0 | 750 | 18 | 77 | 89.6 | 18 | 0.156 | 2106
SOUTH WEST | 25 | 30 | 750 | 1 Door | 675 | 33 | 77 | 89.6 | 38.6 | 0.156 | 4064.58
SOUTH | 25 | 30 | 750 | 0 | 750 | 33 | 77 | 89.6 | 38.6 | 0.156 | 4516.2
SOTH EAST | 25 | 30 | 750 | 1 Door | 675 | 33 | 77 | 89.6 | 38.6 | 0.156 | 4064.58
EAST | 25 | 30 | 750 | 0 | 750 | 18 | 77 | 89.6 | 18 | 0.156 | 2106
NORTH EAST | 25 | 30 | 750 | 1 Door | 675 | 18 | 77 | 89.6 | 18 | 0.156 | 1895.4
[10 empty] | Total | 22754.16
ROOFS
Type | Length (ft) | Area (ft^2) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
Concrete roof on which clay tiles are placed with false ceiling and sound absorbing material | 25 | 3018 | 33 | 0.14 | 13943.16
FLOOR
Type | Length (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load
Concrete flooring with tiles | 25 | 3018 | 9 | 0.345 | 9370.89
DOORS
Type | Length (ft) | Width (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load | 4 Doors
Aluminium Door | 8 | 4 | 32 | 18 | 2.51 | 1445.76 | 5783.04
Calculations for People:-
Type | Persons | SHG/LHG | CLF | Cooling load
Sensible | 250 | 210 | 0.3 | 15750
Latent | 250 | 140 | 1 | 35000
Calculations for Lights:-
Type | Conversion factor | Rated Power | CLF | Ballast Factor | Number of lights | Cooling load
100 W LED bulbs | 3.4 | 100 | 1 | 1.3 | 50 | 22100
Calculations for Appliances:-
Sensible
Type | Conversion factor | Rated Power | CLF | Usage factor | Radiation factor | Quantity | Cooling load
Speakers | 3.4 | 150 | 1 | 1 | 0.15 | 10 | 765
PC | 3.4 | 240 | 0.4 | 0.3 | 0.15 | 1 | 14.688
Projector and UPS | 3.4 | 500 | 0.4 | 0.3 | 0.2 | 1 | 40.8
[6 empty] | Total | 820.488
Calculations for Ventilation:-
Type | Constant | CFM | TD( To-Tc) | Number of persons | Cooling load
Sensible | 1.08 | 5 | 34.2 | 250 | 46170
Type | Constant | CFM | HD( Wo-Wc) | Number of persons | Cooling load
Latent | 4840 | 5 | 0.0185 | 250 | 111925
Calculations for Infiltration:-
Type | Constant | CFM | TD( To-Tc) | Number of persons | Cooling load
Sensible | 1.08 | 5 | 18 | 250 | 24300
Type | Constant | CFM | HD( Wo-Wi) | Number of persons | Cooling load
Latent | 4840 | 5 | 0.0177 | 250 | 107085
Summary
Cooling Load Components | Sensible load | Latent load | TOTAL LOAD IN Btu/hr
WALLS | 22754.16 | 0 | 22754.16
ROOFS | 13943.16 | 0 | 13943.16
FLOOR | 9370.89 | 0 | 9370.89
DOORS | 5783.04 | 0 | 5783.04
LIGHTS | 22100 | 0 | 22100
PEOPLE | 15750 | 35000 | 50750
APPLIANCES | 820.488 | 0 | 820.488
INFILTRATION | 24300 | 107085 | 131385
VENTILATION | 46170 | 111925 | 158095
Total | 160991.738 | 254010 | 415001.738 | TONNES OF REFERIGERATION
Room Total sensible Load | 90521.738 |  |  | 34.5835
Room Total latent Load |  | 35000
Total room load |  |  | 125521.738
Sensible heat factor | 0.72116